ALLIANCE FOR TELECOMMUNICATIONS

INDUSTRY SOLUTIONS

NETWORK RELIABILITY STEERING COMMITTEE

Macro-Analysis:  3rd Quarter 2001

P. J. Aduskevicz

Chair, NRSC

*******************************************************************

1.0  Executive Summary

The Network Reliability Steering Committee (NRSC), under the auspices of the Alliance for Telecommunications Industry Solutions (ATIS), was formed to monitor network reliability utilizing major outage reports filed with the Federal Communications Commission (FCC) per Docket 91-273.  The Committee's mission is to analyze network outage data reported by companies, identify trends, make recommendations aimed at improving network reliability, and make the results publicly available, in order to help ensure a continued high level of network reliability.

Beginning with its First Quarter 2001analysis, the NRSC has made two significant changes in its reporting.  The first is that the baseline for comparison has been changed from a Baseline Year of 7/1/92 – 6/30/93 to a Baseline Period covering the years 1993-2000.  This is being done to better reflect the impact of technological changes that have occurred during the past eight years and to preserve the impact of the outages that have occurred during that period.  The second change is that the “annual” reporting period used by the NRSC has been changed from “mid-year to mid-year” to a calendar year basis.  The reader is urged to take these changes into consideration when making direct comparisons to prior reports.

Considering only data for the third quarter of 2001 (“3Q01”), both the total number of reported outages and the impact of these outages, as measured by the Committee T1-developed outage index (see Figures 2-1 and 2-2), were within the Baseline Period (1993-2000) control limits.  In addition, the number of reported outages in all failure categories except CO Power fell within the “Green” region of the corresponding control chart (see Figures 2-3 to 2-8).  CO Power outages fell within the “Yellow” region. (Note: “Green” is below the upper 95% tolerance limits, “Yellow” is between the upper 95% and 99% tolerance limits, and “Red” is above the upper 99% tolerance limit.)

Analysis of the outages for 3Q01 indicates:

- Outage frequency overall was in the “Green” region.  Within failure categories, all outage frequencies were within the “Green” region except for CO Power, which was in the “Yellow” region.

- While the aggregated outage index overall was in the “Green” region, it is the fourth highest ever (555).  However, if the impact of the World Trade Center attack is discounted, the index drops to 427, near normal for a third quarter.

- The frequency of Facility outages (28) was the highest to date.

- Local Switch outages (11) over the last four quarters were the lowest of any four consecutive quarters.

- The frequency of CO Power outages (28) over the last four quarters were the greatest of any four consecutive quarters.

Based upon analysis of all outages reported from 1Q93 through 3Q01, the NRSC notes that:

- There is an increasing trend in the number of Tandem Switch, CO Power, CCS, and DCS outages.

- There is an increasing trend in the frequency and aggregated outage index of Procedural Errors as the root cause of outages.

There is a decreasing trend in the number of Local Switch outages.

2.0  Quarterly Macro-Analysis

There were 71 initial outage reports filed with the FCC in 3Q01 pursuant to the requirements established in FCC Docket 91-273.  Upon further analysis, the reporting carriers eventually withdrew six (6) of these reports because they did not meet the reporting threshold criteria.  One (1) additional report fell below the 30 minute/30,000-customer threshold and was not included in this analysis because including it would have introduced inconsistent data into the analysis.  In three other instances multiple outage reports were received from carriers for the same outage (13 reports received for four outages). These reports were combined for analysis purposes.  In addition, there was one (1) outage where the reporting carrier filed a Confidentiality Request with the FCC. Taking into consideration the above, the total number of outages analyzed for 3Q01 is 54. (Note: One final report had yet to be received in time for this analysis.  That report is included in the count of outages for this third quarter (54), but is not included in any other analyses.  When received, the appropriate information will be entered into the database and will be reflected in future reports.)

2.1  Summary Statistics

The Baseline Period for this analysis is 1/1/93 to 12/31/00 and was established to benchmark network reliability.  Summary statistics for the years 1993 through 2000, and 3Q01 are shown in Table 1.  (Note: The results for the current quarter are shown as either “w/WTC” or “wo/WTC” where WTC represents the impact of the World Trade Center attack.)

##### Table 1: Summary Statistics

| Year | Total number of outages | Mean time between outages | Median duration of outages | Median outage index | Mean outage index |
| --- | --- | --- | --- | --- | --- |
| 1993 | 157 | 2.32 days | 2.58 hours | 3.33 | 10.07 |
| 1994 | 160 | 2.28 days | 2.50 hours | 3.33 | 10.33 |
| 1995 | 169 | 2.16 days | 3.72 hours | 4.84 | 9.64 |
| 1996 | 174 | 2.10 days | 2.93 hours | 3.16 | 7.64 |
| 1997 | 185 | 1.97 days | 3.38 hours | 3.72 | 8.69 |
| 1998 | 181 | 2.02 days | 2.98 hours | 4.02 | 10.93 |
| 1999 | 176 | 2.07 days | 2.62 hours | 4.00 | 7.59 |
| 2000 | 184 | 1.99 days | 2.23 hours | 3.90 | 8.51 |
| 8-Year Average | 173 | 2.11 days | 2.87 | 3.79 | 9.18 |
| Current Quarter (07/1/01 - 9/30/01) | 54 | 1.70 days w/WTC 1.77days wo/WTC | 3.17 hrs w/WTC 3.00 hrs wo/WTC | 2.57 w/WTC 2.51 wo/WTC | 10.46 w/WTC 8.38 wo/WTC |

Table 2: Failure Category Summary (3Q01)

| Failure Category: | 3Q01 | Seasonal Average |
| --- | --- | --- |
| Local Switch | 2 | 7.3 |
| Tandem Switch | 5 | 5.7 |
| Facility | 28 | 21.1 |
| CO Power | 9 | 5.8 |
| CCS | 5 | 5.6 |
| DCS | 1 | 1.8 |
| Other | 4 | 1.6 |
| Total: | 54 | 48.9 |

2.2 Total Incidents

Figure 2-1 depicts total incidents by quarter for the Baseline Period and the first three quarters of 2001.  A trend line shows that total incident frequency has been increasing since the start of the Baseline Period. The number of outages in 3Q01 (54) is above the third quarter average of 48.9. By comparison, the first quarter average is 39.9, the second quarter 42.0, and the fourth quarter 41.3.

Figure 2-1

FCC Reportable Service Outages
(by number of events)

  - Outage Index

Figure 2-2 depicts the aggregated quarterly outage indexes for the Baseline Period and the first three quarters of 2001. The outage index for this quarter (555) is above the Baseline Period mean (396) and the average third quarter aggregated outage index (420). While the aggregated outage index for this quarter is in the “Green” region, it is the fourth highest since the beginning of the Baseline Period.  However, if the impact of the World Trade Center attack is discounted, the outage index drops to 427, very near the average third quarter index. The average aggregated outage index in the third quarter of the year is higher than the average aggregated outage index in all other quarters.  The first quarter average is 407, the second quarter 393, and the fourth quarter 397. There is a slight upward trend in the aggregated outage index.  If the impacts of the September 11 terrorist attacks are discounted, there is no trend evident.

### Figure 2-2

FCC Reportable Service Outages
(by outage index)

2.4 Failure Category

For 3Q01, all failure categories except CO Power are within or below the “Green” control region. The CO Power category falls in the “Yellow” control region.  The sources of disruptions during this report period were Facility (52%), CO Power (17%), CCS (9%), Tandem Switch (9%), Local Switch (4%), DCS  (2%), and Other 7%.

2.5 Facility Outages

The frequency of Facility outages was in the “Green” region in 3Q01(see Figure 2-3), although just barely.  The number of Facility outages in 3Q01 (28) is the highest ever.  There is no trend in Facility outages since the start of the Baseline Period.  The aggregated outage index for Facility outages in 3Q01 was 245.

Figure 2-3

Incidents by Failure Category
(Facility)

2.6 Local Switch Outages

The number of Local Switch outages reported this quarter (2) is below the mean for the Baseline Period (7.13) (see Figure 2-4).  The average number of Local Switch outages in each of the third quarters over the Baseline Period is 6.7.  The number of Local Switch outages over the last four consecutive quarters (11) is the lowest of any four consecutive quarters since the start of the Baseline Period.  A trend line shows a decreasing trend in Local Switch outages since the start of the Baseline Period.  The aggregated outage index for Local Switch outages in 3Q01 was 8.

Figure 2-4

###### Incidents by Failure Category
(Local Switch)

2.7 Tandem Switch Outages

The number of Tandem Switch outages (5) reported in 3Q01 is near the mean (4.8) for the Baseline Period and below the third quarter average of 5.7 (see Figure 2-5). A trend line shows an increasing trend in Tandem Switch outages since the start of the Baseline Period.  The aggregated outage index for Tandem Switch outages in 3Q01 was 32. (Note: When a Class 5 switch is equipped to function as a 911 tandem, and an outage is reportable due to loss of that functionality, that outage is considered to be a Tandem outage.)

Figure 2-5

###### Incidents by Failure Category

(Tandem Switch)

2.8 CO Power Outages

The number of CO Power outages (9) reported in 3Q01 is above the mean (3.9) for the Baseline Period and is also above the third quarter average of 5.8 (see Figure 2-6).  For the first time, the frequency of CO Power outages is in the “Yellow” region of the control chart. CO Power outage frequency during the warm weather months (second and third quarters of the year) is noticeably higher than in the cold weather months (first and fourth quarters of the year). The number of CO Power outages over the last four consecutive quarters (28) is the greatest of any four consecutive quarters since the beginning of the Baseline Period.  A trend line shows an increasing trend in the frequency of CO Power outages since the start of the Baseline Period.  The aggregated outage index for CO Power outages in 3Q01 was 104.

Incidents by Failure Category
(CO Power)

2.9 Common Channel Signaling Outages

CCS outage frequency (5) in 3Q01 is below the Baseline Period mean of 5.25 and the third quarter average of 5.6 (see Figure 2-7).  A trend line shows that CCS outages exhibit an increasing trend since the start of the Baseline Period.  In addition to the CCS outages reported in 3Q01, there were eleven (11) other outages that impacted signaling capability.  The aggregated outage index for CCS outages in 3Q01 was 24.

Figure 2-7

###### Incidents by Failure Category

###### (Common Channel Signaling)

2.10 Digital Cross-Connect System Outages

There was one (1) DCS outages in 3Q01 (see Figure 2-8), below the Baseline Period average of 1.6 and the third quarter average of 1.8. A trend line shows that DCS outages exhibit an increasing trend since the start of the Baseline Period. Despite this trend DCS outages historically have been a small fraction of outages (3.72% over all quarters).  The aggregated outage index for DCS outages in 3Q01 was 14.

### Figure 2-8

### Incidents by Failure Category

(Digital Cross-Connect Systems)

2.11 Other Results

There were four outages classified as “Other” in 3Q01.  One of these is an outage for which no final report had been received in time for this analysis.  The initial report contains insufficient information to categorize this outage as anything but “Other”.  When the final report is received the appropriate categorization will be entered into the NRSC database and will be reflected in future reports.

Of the remaining three outages, one occurred during the conversion of a central office from a remote to a stand-alone configuration when an inadequate trunk forecast resulted in miscalculation of the number of trunks needed for the tandem trunk group.  The inadequate number of trunks resulted in significant blocking of toll services.

By far the most significant outages in the “Other” category were those associated with the September 11 terrorist attacks.  Nine different carriers with locations in Manhattan that suffered physical damage to their plant filed reports with the FCC in connection with this incident.  More than 300,000 access lines serving more than 14,000 businesses and 20,000 residential customers were directly impacted, and more than 37 million customers were affected indirectly when more than 111 million calls were blocked.  The associated outage index was 123.

One other outage was reported as a result of the September 11 terrorist attacks.  This outage occurred as the result of mass calling following the attacks.  Because of message congestion, the reporting carrier’s SCP servers were intermittently unable to respond to queries, causing 8CXX service calls to time out and fail. The associated outage index was 5.

3.0 Procedural Errors

In addition to categorizing outages by Failure Category and Subcategory, the ATIS/NRSC also categorizes each outage according to its root cause.  Among these root causes are Procedural Errors attributable to Service Providers, System Vendors, and Other Vendors.

Figure 3-1 is a quarterly control chart for Procedural Error outage frequency with control limits derived from Baseline Period data.  In 3Q01, Procedural Error outage frequency was twenty (20), above the Baseline Period mean of 15.2 and the third quarter average of 18.4.  A trend line shows an increasing trend in outages attributed to Procedural Error.

Figure 3-1

#### Procedural Error Attributed Outages

(by number of events)

Figure 3-2 is a quarterly control chart for Procedural Error aggregated outage index.  The Procedural Error outage index for 3Q01 (155) is above the Baseline Period mean of 118 and the third quarter average of 108. A trend line shows an increasing trend in the aggregated outage index for outages with a root cause attributed to Procedural Error.

### Figure 3-2

Procedural Error Attributed Outages

(by outage index)

4.0 Further Observations

In addition to the data on outage frequency and outage impact provided above, the NRSC also makes the following observations as regards outages during the third quarter of 2001:

- Again this quarter there were four outages where the failure of the timing supply was a factor in the outage. While “timing” continues to be a factor in outages each quarter the underlying causes of these outages are generally not similar.  However, two of the outages this quarter were due to the failure of Timing Output Composite Automatic (TOCA) circuit packs.

- During 3Q01, in approximately 30% of the outages analyzed the end-user customer retained dial tone yet lost access to E911 for a portion of or the entire duration of the outage.

- During 3Q01 there were two failures where an earlier failure had placed the equipment in simplex mode.  A second failure occurred prior to the repair of the first resulting in loss of service.  There have been a number of similar situations in the past where an outage occurs during simplex operation.  Service providers are urged to schedule repairs in a timely manner to reduce these occurrences.

5.0 Conclusion

Although both of its primary indicators—the quarterly number of (total) outages and the aggregated quarterly outage index—remain in the “Green” for 3Q01, the NRSC remains concerned with the increasing frequency in Tandem Switch, CO Power, CCS, and DCS outages, and in particular the increases over the last four quarters in CO Power outages.

The NRSC notes that in the past it has investigated CO Power outages and that the Best Practices team of NRIC-IV also investigated CO Power outages.  In both cases it was determined that these outages could have been prevented or their impact mitigated had previously identified Best Practices been followed.  While the most recent group of CO Power outages have not been investigated to the same degree, it is reasonable to assume that the results of the investigation would be the same.

As such, THE NRSC ONCE AGAIN URGES ALL SERVICE PROVIDERS AND EQUIPMENT VENDORS TO REVIEW ALL BEST PRACTICES FOR APPLICATION IN THEIR OPERATIONS.

Appendix K – Memorandum of Understanding

# Footnotes

Addendum A (last revised February 1998) to this report contains additional background on the Network Reliability Council (NRC), outage reporting per FCC Docket 91-273, and the analysis methodology.  Addendum A may be found on the NRSC web site at www.atis.org.

This is a measure of the customer impact based on the number of customers affected, outage duration, and services affected.  See Committee T1 Report No. 42, “A Technical Report on Enhanced Analysis of FCC-Reportable Service Outage Data,” August,1995.

The NRSC defines “Facility” outages as those involving all wiring/cable, associated electronics and hardware (excluding DCSs) and any related work activities associated with these items, from the switch itself to the main frame and from there to and including all outside plant.  Some specific examples include but are not limited to: aerial, underground and submarine cable, radio facilities, repeaters, multiplexers, demultiplexers, regenerators, timing source interface unit, “bits” interface card, and voltage control oscillator fuses.

# Text boxes

The number of reported incidents analyzed this quarter (54) is above the mean for the Baseline Period (43.3), and is also above the seasonal third quarter average of 48.9.

Green

Red

Yellow